Reduced Pressure Principle Assembly Test Procedures

(For use with five-valve equipment) Rev. January 2,2020

Preparation		Notify customer

Inspect area

Flush testcocks (open #4, #3, #2, #1, then close #1, #2, #3, and #4)

Install fittings

Inspect test kit - close all needle valves

Observe CV #1	Attach high hose to testcock #2

Attach low hose to testcock #3

Open testcock #3 slowly then open low-pressure bleed valve

Open testcock #2 slowly then open high-pressure bleed valve

Close high-pressure bleed valve

Close low-pressure bleed valve

(1)	Close #2 shut-off valve, record line pressure

Observe check valve #1 (5.0 psid. or greater to continue)

Record 		Open high control valve two full turns

Relief			Open low control valve slowly (no more than ¼ turn)

Value		(2)	Record relief valve opening  (2.0 psid. or greater to pass)

Close low control valve only

Record CV #2	Bleed bypass hose by opening bypass valve

Leaks			Loosely attach bypass hose to testcock #4

Or			Close bypass valve

Closed			Tighten bypass hose to testcock #4 open testcock #4

Tight			Reset gauge (open and close low-pressure bleed valve)

Open bypass valve two full turns

Observe whether relief valve drips

(3)	Record status of check valve #2 as (closed tight or leaking)

Record #2

Shut-Off		Close testcock #2 observe gauge

Valve		(4)	Record #2 shut-off valve as (closed tight or leaking)

Close bypass valve.

Record CV #1

Open testcock #2, Reset gauge (open and close low-pressure bleed valve)

(5)	Record status of check valve #1 (closed tight or leaked)

(6)	Record value of check valve #1 (5.0 psid. or greater to pass)

(7)	Record buffer value (cv#1 – rv = 3.0 psid. or greater to pass)

Close testcocks #2, #3 and #4 and remove hoses

Record CV #2

Move low hose to testcock #4

Move high hose to testcock #3

Open testcock #4 slowly then open low-pressure bleed valve

Open testcock #3 slowly then open high-pressure bleed valve

Close high-pressure bleed valve

Close low-pressure bleed valve

(8)	Record value of check valve #2 (1.0 psid. or greater to pass)

Final			Close testcocks #3 and #4, remove all equipment

Open #2 shut-off valve slowly

Reduced Pressure Principle Assembly

Trouble Shooting

NOTE:	 Flushing and/or cleaning the internal components can correct many problems. Carefully

observe condition of components.

## PROBLEM					      MAY BE CAUSED BY

Relief valve discharges					1. Faulty check valve #1

continuously				 		2. Faulty check valve #2 with

back-pressure condition

3. Faulty relief valve

Relief valve discharges					1. Properly working assembly with

intermittently						    back-siphonage condition

2. 1st check valve “buffer” is too small

(less than 3.0 psi), with line

pressure fluctuation

3. Water hammer

Relief valve discharges					1. Normally indicates faulty check valve #1

after no. 2 shut-off					    a. dirty or damaged disk

valve is shut. (observe CV #1 test)			    b. dirty or damaged seat

Relief valve would not open,				1. Leaky #2 shut-off valve with

differential on the gage				    	    flow through the assembly

would not drop (relief valve test)

Relief valve would not open,				1. Relief valve stuck closed due to

differential drops to zero				     corrosion or scale

(relief valve test)					2. Relief valve sensing line (s) plugged

Relief valve opens too high				1. Faulty relief valve

(with sufficiently high 1st check reading)		    a. dirty or damaged RV disk

b. dirty or damaged RV seat

1st check reading too low				1. Dirty or damaged CV #1 disk

(less than 3.0 psi “buffer”)				2. Dirty or damaged CV #1 seat

(observe CV #1 test, & Relief valve test)			3. Guide members hanging up

4. Weak or broken CV #1 spring

Leaky 2nd check valve (CV #2 back-pressure test)	1. Dirty or damaged CV #2 disk

2nd check valve reading too low				2. Dirty or damaged CV #2 seat

(CV #2 differential test)					3. Guide members hanging up

4. Weak or broken CV #2 spring

Repair note:	Lubricants shall only be used to assist with the re-assembly of components, and

shall be USDA approved and non-toxic.

Double Check Valve Assembly Test Procedures

(For use with five-valve equipment) Rev. February 26, 2010

Preparation		Notify customer

Inspect area

Flush testcocks

Install fittings

Inspect test kit - close all needle valves

# Note:	Test gauge and hoses must be at same level

CV #1 Test		Install vertical tube on testcock #3

Install compensating tee on testcock #2

Attach high hose to compensating tee installed on testcock #2

Open testcock #2 slowly

Open high-pressure bleed valve then close high-pressure bleed valve

Open testcock #3 to fill vertical tube

Close testcock #3

Close #2 shut-off valve

(1)	Record line pressure

Close #1 shut-off valve

Open testcock #3

- Record status of check valve #1 (closed tight or leaking)

- Record value of check valve #1 (1.0 psid. or greater to pass)

Close testcock #2 and testcock #3

Open #1 shut-off valve to re-pressurize the assembly

CV #2 Test		Move vertical tube from testcock #3 to testcock #4

Move high hose and compensating tee from testcock #2 to testcock #3

Open testcock #3 slowly

Open high-pressure bleed valve then close high-pressure bleed valve

Open testcock #4 to fill vertical tube

Close testcock #4

Close #1 shut-off valve

Open testcock #4

(4)	Record status of check valve #2 as (closed tight or leaking)

(5)	Record value of check valve #2 (1.0 psid. or greater to pass)

Record	(6)(7)	Record #1 & #2 shut-off valve as (closed tight or leaking)

Shut-Off

Valves

Final			Close testcocks #3 and #4, remove all test equipment

Open #1 shut-off valve

Open #2 shut-off valve slowly

Double Check Valve Assembly

Trouble Shooting

With compensating tee arrangement attached to high hose any time water continues to run out of the vertical sight tube you must observe and note gauge reading and prepare to operate the compensating tee in efforts to reduce the flow out of the sight tube to a sight drip.

NOTE:	 Flushing and/or cleaning the internal components can correct many problems. Carefully

observe condition of components.

## PROBLEM					      MAY BE CAUSED BY

During CV #1 test, water stops running 				1. Dirty or damaged CV #1 disk

Out of vertical tube and gauge drops to 0.0 psid.			2. Dirty or damaged CV #1 seat

3. Guide members hanging up

(Leaking CV #1 fix and retest)					4. Weak or broken CV #1 spring

During CV #1 test, water continues running 			1. Leaking CV #2 and leaking

out of vertical tube after compensating  tee runs out of	    	   #2 shut-off valve with

water. (Take observed reading and record CV #1)		   backpressure

During CV #1 test, water continues running 			1. Slightly damaged #1 shut-off

out of vertical tube and it can be controlled to a			    valve

slight drip (Record Check Valve #1)

During CV #1 test, water continues running 			1. Severely damaged #1 shut-off out of vertical tube and it cannot be controlled to a		     valve

slight drip (stop test, resolve problem w/valve and retest)

During CV #1 test, water stops running 				1. Leaking CV #2 and slightly

out of vertical tube and starts to recede into the 		    	    damaged #2 shut-off valve with

tube 								    flow to customer

(Lower equipment to centerline of assembly and record CV #1)

During CV #2 test, water stops running 				1. Dirty or damaged CV #2 disk

out of vertical tube and gauge drops to 0.0 psid.			2. Dirty or damaged CV #2 seat

3. Guide members hanging up

(Leaking CV #2 fix and retest)					4. Weak or broken CV #2 spring

During CV #2 test, water continues running			1. Slightly damaged #1 shut-off

out of vertical tube and it can be controlled to a			     valve

slight drip (Record Check Valve #2)

During CV #2 test, water continues running 			1. Leaking #2 shut-off valve

out of vertical tube after compensating  tee runs out of	    	    with backpressure

water.  (Take observed reading and record CV #2)

During CV #2 test, water stops running 				1. Leaking #2 shut-off valve with

out of vertical tube and starts to recede into the 		   	    flow to customer

tube

(Lower equipment to centerline of assembly and record CV #2)

Repair Note:	Lubricants shall only be used to assist with the re-assembly of components,

and shall be USDA approved and non-toxic.

Pressure Vacuum Breaker Assembly Test Procedures

(For use with five-valve equipment) Rev. February 26, 2010

Preparation		Notify customer

Inspect area

Flush testcocks

Install fittings

Remove air inlet valve canopy

Inspect test kit - close all needle valves

# Note:	Make sure that all hoses and gauge are at the same level as the Pressure Vacuum Breaker

Do not have test kit attached to backflow prevention assembly when opening #1 shut-off valve

Air Inlet Test		Attach high hose to testcock #2

Open testcock #2 slowly

Open high-pressure bleed valve then close high-pressure bleed valve

Close #2 shut-off valve, then close #1 shut-off valve

Slowly open high-pressure bleed valve (no more than ¼ turn) until air inlet valve opens

(1)	Record value of air inlet valve (1.0 psid. or greater to pass)

Close testcock #2 then remove high hose from testcock #2

Close high-pressure bleed valve

Open #1 shut-off valve to re-pressurize the assembly

Check Valve		Attach high hose to testcock #1

Test			Open testcock #1 slowly

Open high-pressure bleed valve then close high-pressure bleed valve

- Record line pressure

Close #1 shut-off valve

Open testcock #2 until water drains out of the body

- Record value of check valve (1.0 psid. or greater to pass)

Record #1	(4)	Record #1 shut-off valve as (closed tight or leaking)

Shut-Off

Valve

Final			Close testcocks #1 and #2, remove all test equipment

Open #1 shut-off valve

Open #2 shut-off valve slowly

Replace air inlet valve canopy

Pressure Vacuum Breaker

Trouble Shooting

NOTE:	 Flushing and/or cleaning the internal components can correct many problems. Carefully

observe condition of components.

## PROBLEM					      MAY BE CAUSED BY

Air inlet valve does not open,				1. Air inlet disk stuck to seat

as gauge drops to 0.0 psid.				2. Broken or missing air inlet spring

3. “Old Style” pressure vacuum breaker

(non-loaded air inlet valve)

Air inlet valve does not open,				1. Leaky #1 shut-off valve

and differential on gauge will				2. Parallel installation with leaky

not drop						    #2 shut-off valve

Air inlet opens below 1.0 psid.				1. Dirty or damage air inlet disk

2. Scale build up on seat

Check valve below 1.0 psid.				1. Dirty or damaged check disk

2. Damaged seat

3. Weak or broken spring

Water runs continuously from				1. Leaky #1 shut-off valve

test cock #2 (CV test)

Repair Note:	Lubricants shall only be used to assist with the re-assembly of components, and

shall be USDA approved and non-toxic.